## Slide 1
Faulted section identification and location
Notes: Please Read this Notice Before you start working with this Template
Please Install the following Fonts and/or make sure its already available on your system.
Aller Font Family or at least Aller Light
Available @ fontsquirell.com
Callibri
Microsoft & Office System Font

## Slide 2
Faulted section identification and location
OUR AGENDA
Protection system flow
1
Application of ANN
2
Training data
3
Faulted section identification
4
Fault location
5

## Slide 3
Protection system flow
1
Tripping action for faulted section
Faulted section identification
Power system
Input data
V, I
Fault detection and classification
Fault type
{ Online }
{ Offline }
Activation function
Faulted section locator
V, I of faulted section
distance

## Slide 4
Protection system flow
1
Application of ANN
2
Preparation of a suitable training data set that represents cases the ANN needs to learn.
Selection of a suitable ANN structure for a given application.
Training the ANN
. Evaluation of the trained ANN using test patterns until its performance is satisfactory
Structure
Training
Evaluation
Pattern

## Slide 5
Protection system flow
1
Application of ANN
2
Input pattern
Output pattern
Training data
3

## Slide 6
Training data
3
Power system
sampling
At 20 KHz
DFT
Discrete Fourier transform
V, I
Extract 3 phase currents and voltages
cases
Large different cases to generate input data

## Slide 7
Training data
3

## Slide 8
Training data
3
Training and testing
Nine measuring points
Three measuring points
This approach has used measurements from all buses taking magnitudes of three-phase currents and voltages as input to the ANN block
This approach has tried to used reduced data in order to reduce complexity and large data transfer
Faulted section identification
4

## Slide 9
Faulted section identification
4
Nine measuring points
Training
moduar ANN faulted section detector | layers | input |  | hidden |  | Output |  | Training | epochs
 |  | neurons | function | neurons | function | neurons | function |  | 
1st approach | 3 | 54 | TANSIG | 30 | TANSING | 6 | PURELIN | 0.986 | 60
2nd approach | 4 | 54 | LOGSIG | 30 , 10 | TANSING | 6 | PURELIN | 0.985 | 56
3rd approach | 3 | 54 | TANSIG | 20 | TANSING | 6 | TANSING | 0.97 | 42
Input (54 neurons)
Faulted section
Hidden (30 neurons)
Current and voltage magnitudes of 3 buses
Output (6 neurons)

## Slide 10
Faulted section identification
4
Nine measuring points
Training
Test

## Slide 11
Effect of the fault location & resistance of modular ANN-based faulted section identifier |  |  |  |  |  |  |  |  |  | 
Section | Fault Type | Fault Location (Km) | Fault Resistance (Ω) | Desired Output |  |  |  |  |  | Status
 |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 
 |  |  |  | Model Output |  |  |  |  |  | 
6_4 | L-L-L | 16.3 | 50 | -0.0010 | 0.0001 | -0.0049 | -0.0018 | 1.0048 | -0.0011 | Accepted
 |  | 71.0 | 50 | 0.0012 | 0.0046 | -0.0011 | 0.0022 | 1.0052 | -0.0078 | Accepted
 |  | 81.6 | 50 | 0.0035 | 0.0090 | 0.0053 | 0.0078 | 0.9986 | -0.0145 | Accepted
 | L-L-G | 61.4 | 50 | 0.0010 | 0.0017 | -0.0035 | -0.0018 | 1.0057 | -0.0026 | Accepted
 |  | 43.2 | 50 | 0.0003 | 0.0016 | -0.0045 | -0.0028 | 1.0055 | -0.0023 | Accepted
 |  | 22.1 | 50 | 0.0003 | -0.0003 | -0.0057 | -0.0016 | 1.0049 | -0.0014 | Accepted
 | Fault Type | Fault Location (Km) | Fault Resistance (Ω) | Desired Output |  |  |  |  |  | Status
 |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 
 |  |  |  | Model Output |  |  |  |  |  | 
 | L-L | 48.0 | 63 | -0.0010 | 0.0003 | 0.0008 | 0.0000 | 1.0040 | -0.0075 | Accepted
 |  | 48.0 | 18 | 0.0010 | 0.0018 | -0.0041 | -0.0024 | 1.0053 | -0.0028 | Accepted
 |  | 48.0 | 29 | 0.0010 | 0.0015 | -0.0035 | -0.0019 | 1.0056 | -0.0029 | Accepted
 | L-G | 48.0 | 0.1 | 0.0000 | 0.0025 | -0.0049 | -0.0038 | 1.0055 | -0.0021 | Accepted
 |  | 48.0 | 48 | 0.0000 | 0.0006 | -0.0041 | -0.0024 | 1.0057 | -0.0025 | Accepted
 |  | 48.0 | 22 | 0.0001 | 0.0021 | -0.0049 | -0.0035 | 1.0054 | -0.0022 | Accepted

## Slide 12
Critical Conditions |  |  |  |  |  |  |  |  |  | 
Section | Fault Type | Fault Location (Km) | Fault Resistance (Ω) | Desired Output |  |  |  |  |  | Status
 |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 
 |  |  |  | Model Output |  |  |  |  |  | 
6_4 | L-L-G | 4.8 | 43 | 0.0027 | -0.0163 | -0.0097 | 0.0142 | 1.0002 | 0.0047 | Accepted
 |  | 25.9 | 35 | 0.0003 | 0.0015 | -0.0055 | -0.0032 | 1.0050 | -0.0018 | Accepted
 |  | 61.4 | 74 | 0.0006 | 0.0005 | -0.0028 | -0.0013 | 1.0058 | -0.0030 | Accepted
 | L-L-L | 86.4 | 23 | 0.0168 | -0.0014 | 0.0062 | 0.0081 | 0.9931 | -0.0078 | Accepted
 |  | 96.0 | 100 | 0.0262 | 0.4679 | 0.0199 | 0.3920 | 0.9062 | -0.6757 | Accepted
 |  | 67.2 | 150 | 0.0000 | 0.5259 | 0.1544 | 0.4451 | 0.7895 | -0.8092 | Rejected

## Slide 13
Faulted section identification
4
Nine measuring points
Training
Test
ANN output at 74Ω, 61.4Km on line 6-4

## Slide 14
Faulted section identification
4
Nine measuring points
Training
Test
ANN output at 14Ω , 34.5KM at line 9-8

## Slide 15
Faulted section identification
4
Nine measuring points
Training
Test
Training
Three measuring points
Training
Modular ANN faulted section identifier | layers | input |  | hidden |  | Output |  | epochs
 |  | neurons | function | neurons | function | neurons | function | 
Bus 1_2_3 | 4 | 18 | LOGSIG | 15,10 | TANSING | 6 | PURELIN | 30
Bus 4_7_9 | 3 | 18 | TANSIG | 15 | TANSING | 6 | PURELIN | 24
Bus 5_6_8 | 3 | 18 | TANSIG | 15 | TANSING | 6 | PURELIN | 21

## Slide 16
Notes: Please Read this Notice Before you start working with this Template
Please Install the following Fonts and/or make sure its already available on your system.
Aller Font Family or at least Aller Light
Available @ fontsquirell.com
Callibri
Microsoft & Office System Font

## Slide 17
Notes: Please Read this Notice Before you start working with this Template
Please Install the following Fonts and/or make sure its already available on your system.
Aller Font Family or at least Aller Light
Available @ fontsquirell.com
Callibri
Microsoft & Office System Font

## Slide 18
Notes: Please Read this Notice Before you start working with this Template
Please Install the following Fonts and/or make sure its already available on your system.
Aller Font Family or at least Aller Light
Available @ fontsquirell.com
Callibri
Microsoft & Office System Font

## Slide 19
Faulted section identification
4
Training
Three measuring points
Test
Effect of the fault location of modular ANN-based faulted section identifier |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
BUS 1,2,3 |  |  |  |  |  | BUS 4,7,9 |  |  |  |  |  | BUS 5,6,8 |  |  |  |  | 
0.945 | -0.006 | 0.028 | -0.002 | -0.045 | 0.125 | 0.894 | 0.002 | 0.125 | 0.002 | -0.016 | -0.011 | 0.860 | 0.023 | 0.141 | -0.025 | -0.019 | 0.004
1.003 | -0.011 | -0.006 | 0.001 | -0.008 | 0.026 | 1.009 | -0.016 | 0.023 | 0.013 | -0.027 | -0.007 | 0.904 | 0.008 | 0.094 | -0.007 | -0.008 | -0.010
1.010 | -0.010 | -0.003 | 0.002 | 0.005 | -0.012 | 1.028 | -0.028 | 0.002 | 0.015 | -0.026 | 0.002 | 0.962 | -0.010 | 0.035 | 0.010 | 0.006 | -0.024
1.011 | -0.009 | -0.003 | 0.002 | 0.006 | -0.015 | 1.021 | -0.008 | 0.019 | -0.010 | -0.029 | 0.009 | 0.987 | -0.030 | 0.005 | -0.050 | 0.006 | 0.062
1.006 | -0.011 | -0.002 | 0.005 | 0.005 | -0.010 | 1.026 | -0.018 | -0.025 | -0.002 | 0.012 | 0.005 | 1.009 | 0.003 | 0.006 | -0.019 | -0.004 | 0.022
0.812 | 0.208 | -0.005 | -0.012 | 0.006 | -0.017 | 0.922 | 0.087 | 0.000 | -0.008 | -0.008 | 0.009 | 0.991 | 0.125 | -0.025 | -0.020 | -0.087 | 0.010
Effect of the fault location of modular ANN-based faulted section identifier |  |  |  |  |  |  |  |  |  | 
Section | Fault Type | Fault Location (Km) | Fault Resistance (Ω) | Desired Output |  |  |  |  |  | Status
 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 
 |  |  |  | Model Output |  |  |  |  |  | 
7_5 | L-G | 21.2 | 50 | 0.9831 | 0.0021 | -0.0093 | -0.0047 | 0.0198 | 0.0036 | Accepted
 |  | 44.2 | 50 | 1.0182 | 0.0121 | -0.0487 | 0.0044 | 0.0149 | -0.0050 | Accepted
 |  | 79.5 | 0 | 1.0117 | 0.0104 | -0.0335 | 0.0125 | 0.0034 | -0.0060 | Accepted
 | L-L | 93.7 | 50 | 1.0064 | 0.0097 | -0.0095 | 0.0107 | -0.0113 | -0.0153 | Accepted
 |  | 152.0 | 50 | 1.0064 | -0.0073 | 0.0249 | 0.0155 | -0.0019 | -0.0213 | Accepted
 |  | 67.1 | 0 | 1.0035 | -0.0020 | -0.0023 | 0.0005 | -0.0011 | -0.0011 | Accepted

## Slide 20
Faulted section identification
4
Training
Three measuring points
Test
Effect of the fault resistance of modular ANN-based faulted section identifier |  |  |  |  |  |  |  |  |  | 
Section | Fault Type | Fault Location (Km) | Fault Resistance (Ω) | Desired Output |  |  |  |  |  | Status
 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 
 |  |  |  | Model Output |  |  |  |  |  | 
7_5 | L-L-G | 88.4 | 0.1 | 1.0046 | 0.0027 | -0.0045 | 0.0024 | -0.0018 | -0.0057 | Accepted
 |  | 88.4 | 5 | 0.8689 | -0.0304 | 0.2107 | 0.0541 | 0.0000 | -0.0486 | Accepted
 |  | 88.4 | 15 | 0.7253 | -0.0396 | 0.4104 | 0.0745 | -0.0215 | -0.0738 | Rejected
 | L-L-L | 88.4 | 29 | 0.5830 | -0.0556 | 0.3802 | -0.0177 | 0.0692 | -0.0014 | Rejected
 |  | 88.4 | 46 | 1.0165 | 0.0364 | -0.0338 | 0.0045 | -0.0324 | 0.0117 | Accepted
 |  | 88.4 | 70 | 1.3041 | 0.0688 | -0.3520 | -0.0463 | 0.0068 | 0.0134 | Rejected
Effect of the fault resistance of modular ANN-based faulted section identifier |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
BUS 1,2,3 |  |  |  |  |  | BUS 4,7,9 |  |  |  |  |  | BUS 5,6,8 |  |  |  |  | 
1.007 | -0.009 | -0.002 | 0.005 | 0.006 | -0.015 | 1.025 | -0.019 | -0.024 | -0.001 | 0.012 | 0.003 | 0.950 | 0.017 | 0.069 | -0.003 | -0.002 | -0.006
1.008 | -0.008 | -0.003 | 0.005 | 0.006 | -0.016 | 1.026 | -0.020 | -0.024 | 0.002 | 0.010 | 0.002 | 0.931 | 0.019 | 0.090 | -0.013 | -0.001 | 0.001
1.009 | -0.008 | -0.003 | 0.004 | 0.006 | -0.016 | 1.027 | -0.023 | -0.023 | 0.011 | 0.006 | 0.000 | 0.926 | 0.008 | 0.094 | 0.003 | 0.009 | -0.014
1.006 | -0.011 | -0.003 | 0.004 | 0.004 | -0.007 | 1.015 | 0.001 | -0.020 | 0.007 | 0.021 | -0.022 | 0.912 | 0.043 | 0.097 | -0.103 | -0.050 | 0.115
1.007 | -0.011 | -0.003 | 0.004 | 0.004 | -0.009 | 1.011 | 0.008 | 0.002 | 0.011 | -0.001 | -0.028 | 0.979 | -0.032 | 0.017 | -0.022 | -0.002 | 0.051
1.007 | -0.010 | -0.003 | 0.004 | 0.004 | -0.010 | 0.998 | 0.008 | 0.081 | 0.091 | -0.093 | -0.084 | 0.926 | -0.111 | 0.057 | 0.069 | 0.048 | -0.023

## Slide 21
Faulted section identification
4
Training
Three measuring points
Test
Critical Conditions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
BUS 1,2,3 |  |  |  |  |  | BUS 4,7,9 |  |  |  |  |  | BUS 5,6,8 |  |  |  |  | 
0.669 | 0.341 | -0.003 | -0.006 | 0.004 | -0.013 | 1.016 | -0.011 | -0.025 | 0.002 | 0.016 | -0.005 | 1.001 | 0.017 | 0.019 | 0.028 | 0.003 | -0.037
0.022 | 0.968 | 0.002 | 0.005 | -0.001 | 0.002 | 0.883 | 0.127 | -0.022 | -0.009 | 0.019 | -0.001 | 0.893 | 0.152 | 0.047 | 0.218 | -0.073 | -0.217
1.016 | -0.007 | -0.004 | -0.004 | 0.006 | -0.018 | 1.026 | -0.021 | -0.010 | 0.009 | -0.008 | 0.002 | 1.066 | 0.002 | -0.061 | 0.024 | 0.016 | -0.035
1.008 | -0.011 | -0.004 | 0.002 | 0.002 | -0.003 | 1.023 | -0.024 | 0.008 | 0.022 | -0.027 | -0.007 | 0.934 | -0.002 | 0.063 | 0.003 | 0.000 | -0.018
0.987 | -0.008 | 0.000 | 0.000 | -0.024 | 0.067 | 0.944 | -0.007 | 0.062 | 0.050 | -0.013 | -0.043 | 0.866 | 0.007 | 0.131 | -0.007 | -0.008 | -0.007
0.871 | 0.141 | -0.004 | -0.004 | 0.006 | -0.017 | 0.844 | 0.143 | 0.006 | 0.029 | -0.042 | 0.006 | 0.867 | 0.138 | 0.115 | -0.017 | -0.073 | -0.014
Critical Conditions |  |  |  |  |  |  |  |  |  | 
Section | Fault Type | Fault Location (Km) | Fault Resistance (Ω) | Desired Output |  |  |  |  |  | Status
 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 
 |  |  |  | Model Output |  |  |  |  |  | 
7_5 | L-L | 150.2 | 0.5 | 1.0980 | -0.0099 | -0.0736 | 0.0068 | -0.0064 | -0.0135 | Accepted
 |  | 169.6 | 8 | 0.7049 | 0.2217 | 0.0287 | -0.0618 | 0.0048 | 0.0726 | Rejected
 |  | 113.1 | 32 | 0.5134 | -0.0556 | 0.7993 | 0.0550 | -0.2477 | -0.0897 | Rejected
 | L-G | 63.6 | 55 | 1.0768 | -0.0110 | -0.0893 | -0.0029 | 0.0270 | -0.0168 | Accepted
 |  | 33.6 | 65 | 1.1048 | 0.0117 | -0.1680 | -0.0238 | 0.0740 | -0.0484 | Accepted
 |  | 144.9 | 80 | 1.2150 | 0.0733 | -0.2939 | 0.0562 | 0.0386 | -0.1792 | Accepted

## Slide 25
Fault location
5

## Slide 26
Fault location
5
Isolating the faulted section
Fault location activation
Three phase currents and voltage from both ends are fed to ANN
Step
02
Step
01
Step
03
Fault distance (Km)
offline

## Slide 27
Fault location
5
offline
Training
fault distance (%) | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
desired output | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1

## Slide 28
Fault location
5
offline
Training
Testing
Fault conditions |  |  |  |  | 
Section | Fault type | Fault resistance (Ω) | Desired output(Km) | Actual output(Km) | Error
7_5 | L-G | 10 | 80.50 | 86.098 | 0.032
 |  | 55 | 63.3 | 64.180 | 0.005
 |  | 65 | 33.6 | 35.673 | 0.012
 |  | 80 | 145 | 131.840 | 0.074
 |  | 0.5 | 50 | 51.130 | 0.006
 | L-L-G | 21 | 83 | 87.263 | 0.024
 |  | 80 | 94.7 | 98.667 | 0.022
 |  | 27 | 170 | 173.717 | 0.021
 |  | 12 | 76.93 | 84.674 | 0.044
 |  | 34 | 45.5 | 44.030 | 0.008
 | L-L | 8 | 169 | 176.181 | 0.041
 |  | 42 | 38.46 | 33.489 | 0.028
 |  | 134 | 93.6 | 92.594 | 0.006
 |  | 32 | 113 | 112.643 | 0.002
 |  | 0.5 | 150 | 151.823 | 0.010
 | L-L-L | 21 | 68 | 96.747 | 0.163
 |  | 150 | 100 | 105.642 | 0.032
 |  | 0.5 | 60 | 62.232 | 0.013
 |  | 8 | 9 | 12.172 | 0.018
 |  | 200 | 92 | 101.755 | 0.055